## ABB tag list
Tank | Inputs/Output | Tag | Description | IO_Type | Signal Range/Type | Function_Role
Raw Tank | Input | ai_LT_RT_001 | Water Level Transmitter | Analog In | 4-20 mA Continuous | water level measurement for process control
Raw Tank | Input | di_LAH_RT_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm for high water level to prevent overflow
Raw Tank | Input | di_LSL_RT_001 | Low Level Switch | Digital In | On/Off (0/1) | Alarm/interlock for low water level
Raw Tank | Input | ai_SLS_RT_001 | Sludge Level Sensor | Analog In | 4-20 mA Continuous | sludge blanket level monitoring
Raw Tank | Input | di_TRIP_PUMP_RT_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Alarm for raw water pump failure
Raw Tank | Input | di_TRP_ST_001 | Sludge Pump Trip Alarm | Digital In | On/Off (0/1) | Alarm for sludge pump failure
Raw Tank | Output | do_CV_RT_001 | Inlet Control Valve | Digital Out | Open/Close (0/1) | Controls water inlet to raw water tank
Raw Tank | Output | do_PUMP_INT_RT_001 | Inlet Pump | Digital Out | On/Off (0/1) | Pumps raw water into the tank
Raw Tank | Output | do_OCV_RT_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Controls raw water outlet flow
Raw Tank | Output | do_CV_SLUDGE_RT_001 | Sludge Outlet Valve | Digital Out | Open/Close (0/1) | Regulates sludge discharge to sludge pump
Raw Tank | Output | do_SLPUM_RT_001 | Sludge Pump | Digital Out | On/Off (0/1) | Runs sludge pump to clear settled sludge
Aeration Tank | Input | ai_LT_AT_001 | Water Level Transmitter | Analog In | 4-20 mA Continuous | measurement of aeration tank water level
Aeration Tank | Input | di_LAH_AT_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm for high water level to prevent overflow
Aeration Tank | Input | di_LSL_AT_001 | Low Level Switch | Digital In | On/Off (0/1) | Alarm or interlock at low water level
Aeration Tank | Input | ai_DO_AT_001 | Dissolved Oxygen Sensor | Analog In | 4-20 mA | Measures oxygen concentration in aeration tank
Aeration Tank | Input | ai_BOD_AT_001 | Biochemical Oxygen Demand Sensor | Analog In | 4-20 mA or digital | Monitors organic load concentration for process control
Aeration Tank | Output | do_BLOWER_AT_001 | Aeration Blower Control | Digital Out | On/Off, VFD speed | Controls blower operation to maintain oxygen level
Aeration Tank | Output | do_AIRVALVE_AT_001 | Aeration Air Control Valve | Digital Out | Open/Close (0/1) | Regulates airflow through aeration diffusers
Aeration Tank | Output | do_MIXER_AT_001 | Mixer Motor | Digital Out | On/Off | Ensures agitation for mixing oxygen and microbes
Aeration Tank | Output | do_OCV_AT_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Controls flow of treated water from the aeration tank
Aeration Tank | Output | do_PUMP_INT_AT_001 | Inlet Pump | Digital Out | On/Off (0/1) | Pumps influent water into the aeration tank
Aeration Tank | Input | di_TRIP_PUMP_AT_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Detects pump fault conditions and triggers alarms
Aeration Tank | Input | di_ALM_DO_AT_001 | DO Range Alarm | Digital In | On/Off (0/1) | Alarm if dissolved oxygen is out of preset operational range
Aeration Tank | Input | di_ALM_BOD_AT_001 | BOD High Alarm | Digital In | On/Off (0/1) | Alarm if biochemical oxygen demand exceeds safe limit
Secondary Tank | Input | ai_LT_ST_001 | Water Level Transmitter | Analog In | 4-20 mA Continuous | water level measurement in tank
Secondary Tank | Input | di_LAH_ST_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm for high water level to prevent overflow
Secondary Tank | Input | di_LSL_ST_001 | Low Level Switch | Digital In | On/Off (0/1) | Low level alarm/interlock to protect pumps
Secondary Tank | Input | ai_SLS_ST_001 | Sludge Level Sensor | Analog In | 4-20 mA Continuous | sludge blanket measurement (interface)
Secondary Tank | Input | di_TRP_ST_001 | Sludge Pump Trip Alarm | Digital In | On/Off (0/1) | Pump fault detection
Secondary Tank | Input | di_TRIP_PUMP_ST_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Motor fault/trip alarm for pump or valve motor
Secondary Tank | Output | do_PUMP_INT_ST_001 | Inlet Pump | Digital Out | On/Off (0/1) | Pump to feed raw or treated water into the tank
Secondary Tank | Output | do_SLPUM_ST_001 | Sludge Pump | Digital Out | On/Off (0/1) | Pump to remove settled sludge from tank bottom
Secondary Tank | Output | do_OCV_ST_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Outlet water to next process (e.g., dosing tank)
Secondary Tank | Output | do_CV_SLUDGE_RT_001 | Sludge Outlet Valve | Digital Out | Open/Close (0/1) | Dedicated sludge removal outlet valve
Dosing Pump Run | Input | ai_PH_DT_001 | pH Sensor | Analog In | 4-20 mA (0-14 pH) | Monitors pH level for chemical dosing control
Dosing Pump Run | Output | do_OCV_DT_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Controls treated water outflow to next stage
Dosing Pump Run | Output | do_ACIDP_DT_001 | Acid Dosing Pump Run | Digital Out | On/Off (0/1) | Runs acid dosing pump for pH reduction
Dosing Pump Run | Output | do_BASEP_DT_001 | Base Dosing Pump Run | Digital Out | On/Off (0/1) | Runs base dosing pump for pH increase
Dosing Pump Run | Input | di_APS_DT_001 | Acid Pump Status | Digital In | On/Off (0/1) | Confirms status/feedback of acid dosing pump
Dosing Pump Run | Input | di_BPS_DT_001 | Base Pump Status | Digital In | On/Off (0/1) | Confirms status/feedback of base dosing pump
Dosing Pump Run | Output | do_PH_ALM_DT_001 | pH Out-of-Range Alarm | Digital Out | On/Off (0/1) | Indicates alarm when pH is out of permitted range
Dosing Pump Run | Input | ai_LT_ST_001 | Water Level Transmitter | Analog In | 4-20 mA | Continuous water level measurement in tank
Dosing Pump Run | Input | di_LAH_ST_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm for high water level to prevent overflow
Dosing Pump Run | Input | di_LSL_ST_001 | Low Level Switch | Digital In | On/Off (0/1) | Low level alarm/interlock to protect pumps
Dosing Pump Run | Output | do_PUMP_INT_DT_001 | Inlet Pump | Digital Out | On/Off (0/1) | Controls raw or treated water feed pump operation
Dosing Pump Run | Input | di_TRIP_PUMP_DT_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Detects fault/trip condition on input pump; triggers alarm and pump shutdown
Disinfectant Tank | Input | ai_LT_DT_001 | Water Level Transmitter | Analog In | 4-20 mA | Continuous water level measurement in the tank
Disinfectant Tank | Input | di_LAH_DT_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm if water level exceeds safe maximum
Disinfectant Tank | Input | di_LSL_DT_001 | Low Level Switch | Digital In | On/Off (0/1) | Alarm/interlock if water level too low
Disinfectant Tank | Output | do_OCV_DIT_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Controls disinfected water flow downstream
Disinfectant Tank | Output | do_PUMP_INT_DIT_001 | Inlet Pump | Digital Out | On/Off (0/1) | Controls raw or treated water feed pump operation
Disinfectant Tank | Output | do_PUMP_DIT_002 | Disinfectant Dosing Pump | Digital Out | On/Off (0/1) | Controls chemical disinfectant dosing
Disinfectant Tank | Input | di_ALM_DIT_001 | Disinfectant Pump Fault Alarm | Digital In | On/Off (0/1) | Alarm on failure of disinfectant dosing pump
Disinfectant Tank | Output | do_MIXER_DIT_001 | Mixer Motor | Digital Out | On/Off | Ensures uniform dispersal of disinfectant
Disinfectant Tank | Input | ai_RS_DIT_001 | Disinfectant Residual Sensor | Analog In | 4-20 mA | Measures disinfectant residual concentration
Disinfectant Tank | Input | di_LR_ALM_DT_002 | Low Residual Alarm | Digital In | On/Off | Alarm if disinfectant residual below effective level
Disinfectant Tank | Input | di_HR_ALM_DT_003 | High Residual Alarm | Digital In | On/Off | Alarm if disinfectant residual exceeds safe level
Disinfectant Tank | Input | di_TRIP_PUMP_DIT_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Alarm for issues or fault in input pump
Pure Water Tank | Input | ai_LT_PWT_001 | Water Level Transmitter | Analog In | 4-20 mA | Continuous measurement of purified water level in tank
Pure Water Tank | Input | di_LAH_PWT_001 | High Level Alarm | Digital In | On/Off (0/1) | Alarm to prevent overflow of purified water tank
Pure Water Tank | Input | di_LSL_PWT_001 | Low Level Switch | Digital In | On/Off (0/1) | Low level alarm/interlock to protect feeding pumps
Pure Water Tank | Input | di_TRIP_PUMP_PWT_001 | Input Pump Trip Alarm | Digital In | On/Off (0/1) | Indicates fault or trip on purified water pump
Pure Water Tank | Output | do_PUMP_INT_PWT_001 | Inlet Pump | Digital Out | On/Off (0/1) | Pump to feed purified water from tank to downstream process
Pure Water Tank | Output | do_OCV_PWT_001 | Water Outlet Valve | Digital Out | Open/Close (0/1) | Controls flow of purified water exiting the tank